## Bact1
Test Report
Client: | Kareeberg Municipality |  |  |  |  | page 1 of 4
Reference: | 83342
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-02-21
Date sampled: | 2011-02-21
Determinand | Sample number: | SANS 241:2006 specifications | Kareeberg Municipaliteit Carnarvon Hospitaal | Kareeberg Municipaliteit Carnarvon Kliniek | Kareeberg Munisipaliteit Van Wyksvlei Munisipale Kantoor | Kareeberg Municipaliteit Vosburg Munisipale Kantoor
| Lab number: |  | K1 | K2 | K3 | K4
| Units | value | Value | Value | Value | Value
Heterotrophic plate count | cfu/ml | 100
Total coliforms | cfu/ml | 0 | 31 | 19 | 0 | >201
E.coli | cfu/100ml | 0 | 0 | 0 | 0 | 0
Bacterial note: Parameters higher than specifications are clearly indicated.
Signed: ___________________________ | [5 empty] | Date issued: 21 February 2011
H Human
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za

## Bact2 (2)
Test Report
Client: | Kareeberg Municipality |  |  | page 2 of 4
Reference: | 83342
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-02-21
Date sampled: | 2011-02-21
Determinand | Sample number: | DWAF sewage effluent specifications | Kareeberg Maturation Pond | Kareeberg Anaërobiese damme
| Lab number: |  | K5 | K6
| Units | value | Value | Value
Heterotrophic plate count | cfu/ml
Faecal coliform | cfu/ml | 1000 | >2419 | >2419
E.coli | cfu/100ml | 0 | 387 | >2419
Chemistry note: no chemistry
Bacterial note: Parameters higher than specifications are clearly indicated.
Signed: ___________________________ |  |  |  | Date issued: 21 February 2011
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za

## Sewage
Test Report
Client: | Kareeberg Municipality |  |  | page 3 of 4
Reference: | 83342
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-02-21
Date sampled: | 2011-02-21
Determinand | Sample number | Section 39 of the National Water Act of 1998 | Kareeberg - Maturation Pond | Kareeberg - Anaërobiese Damme
| Lab nr. | General Limit | 1 | 2
| Units | Value | Value | Value
pH |  | 5.5 - 9.5
Electrical conductivity | mS/m | 70 - 150 mS/m above intake
Ammonia (NH3) as N | mg/L | 6
Chemical Oxygen Demand (COD) | mg/L | 75
Nitrate (NO3)/ Nitrite (NO2) as N | mg/L | 15
Ortophosphate (PO4) as P | mg/L | 10
Suspendid Solids(SS) | mg/L | 25
Faecal coliforms | cfu/100ml | 1000
E.coli | cfu/100ml
Signed: ___________________________ |  |  |  | Date issued: February 2011
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za

## Drinking
Test report
Client: | Kareeberg Municipality |  |  |  |  | Page 4 of 4
Reference: | 83342
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-02-21
Date sampled: | 2011-02-21
Determinand | Sample number: | Carnarvon Kliniek | Van Wyksvlei Munisipale Kantore | Vosburg Munisipale Kantore | South African National Standard (SANS) 241:2006 for drinking water
| Lab number: | Carnarvon Kliniek | Van Wyksvlei Munisipale Kantore | Vosburg Munisipale Kantore | Class 1 (Recommended levels) | Class 2 (Maximum allowable for limited time)
| Units | Value | Value | Value | Value | Value
Chemical report
pH |  |  |  |  | 5.5 tot 9.5 | <4 en >10
Electrical conductivity | mS/m |  |  |  | 150 | 370
Calcium as Ca | mg/L |  |  |  | 150 | 300
Magnesium as Mg | mg/L |  |  |  | 70 | 100
Sodium as Na | mg/L |  |  |  | 200 | 400
Potassium as K | mg/L |  |  |  | 50 | 100
P-Alkalinity | mg/L
M-Alkalinity | mg/L
Fluoride as F | mg/L |  |  |  | 1 | 1.5
Chloride as Cl | mg/L |  |  |  | 200 | 600
Bromide as Br | mg/L |  |  |  | **3 | **6
Nitrate as N | mg/L |  |  |  | 10 | 20
Phosphate as PO4 | mg/L |  |  |  |  | *15.33
Sulphate as SO4 | mg/L |  |  |  | 400 | 600
Calcium Hardness | mg/L |  |  |  | 375 | 750
Magnesium Hardness | mg/L |  |  |  | 287 | 410
Total Hardness as CaCO3 | mg/L |  |  |  | 662 | 1160
Total Dissolved Solids | mg/L |  |  |  | 1050 | 2590
Aluminium as Al | mg/L |  |  |  | 0.3 | 0.5
Arsenic as As | mg/L |  |  |  | 0.01 | 0.05
Chromium as Cr | mg/L |  |  |  | 0.1 | 0.5
Copper as Cu | mg/L |  |  |  | 1 | 2
Iron as Fe | mg/L |  |  |  | 0.2 | 2
Manganese as Mn | mg/L |  |  |  | 0.1 | 1
Lead as Pb | mg/L |  |  |  | 0.02 | 0.05 | 5
Zinc as Zn | mg/L |  |  |  | 5 | 10
Chemistry note: According to these results, most of the parameters tested are within the drinking water limits.Those higher are clearly marked.
Bacteriology: The bacteriology results are reflected on other worksheets in this file.
Signed: ___________________________ | [5 empty] | Date issued: February 2011
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
From: DWAF Domestic use guidelines
Hardness Range | Description of Hardness
0 - 50 | Soft
50 - 100 | Moderately soft
100 - 150 | Slightly hard
150 - 200 | Moderately hard
200 - 300 | Hard
> 300 | Very hard
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za