## Bact1
Test Report
Client: | Kareeberg Municipality |  |  |  |  | Page 1 of 3
Reference: | 83488
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-04-19
Date sampled: | 2011-04-19
Determinand | Sample number: | SANS 241:2006 specifications | Kareeberg Municipaliteit Carnarvon Hospitaal | Kareeberg Municipaliteit Carnarvon Kliniek | Kareeberg Municipaliteit Van Wyksvlei Munisipale Kantoor | Kareeberg Munisipaliteit Vosburg Munisipale Kantoor
| Lab number: |  | U1 | U2 | U3 | U4
| Units | value | Value | Value | Value | Value
Heterotrophic plate count | cfu/ml | 100 | 0 | 1 | >2500 | 18
Total coliforms | cfu/ml | 0 | 0 | 2 | >201 | 165
E.coli | cfu/100ml | 0 | 0 | 0 | 0 | 0
Bacterial note: Parameters higher than specifications are clearly indicated.
Signed: ___________________________ | [5 empty] | Date issued: 20 April 2011
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za

## drink
Test report
Client: | Kareeberg Municipality |  |  |  | Page 2 of 3
Reference: | 83488
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-04-19
Date sampled: | 2011-04-19
Determinand | Sample number: | Carnarvon Kliniek | Vosburg Munisipale Kantore | South African National Standard (SANS) 241:2006 for drinking water
| Lab number: | Carnarvon Kliniek | Vosburg Munisipale Kantore | Class 1 (Recommended levels) | Class 2 (Maximum allowable for limited time)
| Units | Value | Value | Value | Value
Chemical report
pH |  | 7.9 | 7.7 | 5.5 tot 9.5 | <4 en >10
Electrical conductivity | mS/m | 62.5 | 112 | 150 | 370
Calcium as Ca | mg/L | 25.0546 | 68.5379 | 150 | 300
Magnesium as Mg | mg/L | 20.2066 | 34.1539 | 70 | 100
Sodium as Na | mg/L | 76.871 | 110.9972 | 200 | 400
Potassium as K | mg/L | 1.1915 | 2.1028 | 50 | 100
P-Alkalinity | mg/L | 0 | 0
M-Alkalinity | mg/L | 262 | 295
Fluoride as F | mg/L | 0.99 | 0.68 | 1 | 1.5
Chloride as Cl | mg/L | 24 | 142 | 200 | 600
Bromide as Br | mg/L | <0.04 | <0.04 | **3 | **6
Nitrate as N | mg/L | 1.39 | 2.53 | 10 | 20
Phosphate as PO4 | mg/L | <0.1 | <0.1 |  | *15.33
Sulphate as SO4 | mg/L | 31 | 89 | 400 | 600
Calcium Hardness | mg/L | 62.6364 | 171.3449 | 375 | 750
Magnesium Hardness | mg/L | 82.847 | 140.031 | 287 | 410
Total Hardness as CaCO3 | mg/L | 145.4835 | 311.3758 | 662 | 1160
Total Dissolved Solids | mg/L | 447.4666 | 753.6711 | 1050 | 2590
Aluminium as Al | mg/L | <0.004 | 0.014 | 0.3 | 0.5
Arsenic as As | mg/L | <0.006 | <0.006 | 0.01 | 0.05
Chromium as Cr | mg/L | <0.006 | <0.006 | 0.1 | 0.5
Copper as Cu | mg/L | 0.021 | 0.019 | 1 | 2
Iron as Fe | mg/L | 0.004 | 0.008 | 0.2 | 2
Manganese as Mn | mg/L | 0.001 | 0.012 | 0.1 | 1
Lead as Pb | mg/L | <0.010 | <0.010 | 0.02 | 0.05 | 5
Zinc as Zn | mg/L | 0.029 | 0.018 | 5 | 10
Chemistry note: According to these results, all of the parameters tested are within the drinking water limits
Bacteriology: The bacteriology results are reflected on other worksheets in this file.
Signed: ___________________________ |  |  |  |  | Date issued: 4 May 2011
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
From: DWAF Domestic use guidelines
Hardness Range | Description of Hardness
0 - 50 | Soft
50 - 100 | Moderately soft
100 - 150 | Slightly hard
150 - 200 | Moderately hard
200 - 300 | Hard
> 300 | Very hard
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za

## Sewage
Test Report
Client: | Kareeberg Municipality |  |  | Page 3 of 3
Reference: | 83488
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-04-19
Date sampled: | 2011-04-19
Determinand | Sample number | Section 39 of the National Water Act of 1998 | Maturation Pond | Anaërobiese Dam
| Lab nr. | General Limit | C1 | C3
| Units | Value | Value | Value
pH |  | 5.5 - 9.5 | 8.79 | 7.72 | 28
Electrical conductivity | mS/m | 70 - 150 mS/m above intake | 147 | 132 | 28
Ammonia (NH3) as N | mg/L | 6 | 21.221 | 60.667 | 65
Chemical Oxygen Demand (COD) | mg/L | 75 | 246 | 372 | 95
Nitrate (NO3)/ Nitrite (NO2) as N | mg/L | 15 | 0.23 | 0.1 | 49
Ortophosphate (PO4) as P | mg/L | 10 | 12.04 | 6.23 | 49
Suspendid Solids(SS) | mg/L | 25 | 91.6 | 134 | 65
Faecal coliforms | cfu/100ml | 1000 | >2419 | >2419 | 379
E.coli | cfu/100ml |  | >2419 | >2419
Signed: ___________________________ |  |  |  | Date issued: 28 April 2011
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za