## Bact1
Test Report
Client: | Kareeberg Municipality |  |  |  |  | Page 1 of 2
Reference: | 83489
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-05-10
Date sampled: | 2011-05-10
Determinand | Sample number: | SANS 241:2006 specifications | Kareeberg Municipaliteit Carnarvon Kliniek | Kareeberg Municipaliteit Carnarvon Hospitaal | Kareeberg Municipaliteit Van Wyksvlei Munisipale Kantoor | Kareeberg Munisipaliteit Vosburg Munisipale Kantoor
| Lab number: |  | U1 | U2 | U3 | U4
| Units | value | Value | Value | Value | Value
Heterotrophic plate count | cfu/ml | 100 | 3 | 2 | 517 | 24
Total coliforms | cfu/ml | 0 | 2 | 3 | 3 | 66
E.coli | cfu/100ml | 0 | 0 | 0 | 0 | 0
Bacterial note: Parameters higher than specifications are clearly indicated.
Signed: ___________________________ | [5 empty] | Date issued: 12 May 2011
H Human
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za

## drink
Test report
Client: | Kareeberg Municipality |  |  |  |  | Page 2 of 2
Reference: | 83489
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-05-10
Date sampled: | 2011-05-10
Determinand | Sample number: | Carnarvon Hospitaal | Van Wyksvlei Mun. Kantoor | Vosburg Munisipale Kantore | South African National Standard (SANS) 241:2006 for drinking water
| Lab number: | Carnarvon Hospitaal | Van Wyksvlei Mun. Kantoor | Vosburg Munisipale Kantore | Class 1 (Recommended levels) | Class 2 (Maximum allowable for limited time)
| Units | Value | Value | Value | Value | Value
Chemical report
pH |  | 7.87 | 6.33 | 7.66 | 5.5 tot 9.5 | <4 en >10
Electrical conductivity | mS/m | 66.8 | 10.9 | 106 | 150 | 370
Calcium as Ca | mg/L | 26.8049 | 1.6049 | 62.8942 | 150 | 300
Magnesium as Mg | mg/L | 24.2363 | 1.2501 | 36.1554 | 70 | 100
Sodium as Na | mg/L | 87.7758 | 17.5462 | 109.4041 | 200 | 400
Potassium as K | mg/L | 0.52208 | 0.38446 | 1.9099 | 50 | 100
P-Alkalinity | mg/L | 0 | 0 | 0
M-Alkalinity | mg/L | 266 | 10.8 | 287
Fluoride as F | mg/L | 0.95 | 0.09 | 0.76 | 1 | 1.5
Chloride as Cl | mg/L | 29 | 24 | 123 | 200 | 600
Bromide as Br | mg/L | <0.04 | <0.04 | <0.04 | **3 | **6
Nitrate as N | mg/L | 0.87 | 0.05 | 2.23 | 10 | 20
Phosphate as PO4 | mg/L | 0.67 | 0.28 | <0.1 |  | *15.33
Sulphate as SO4 | mg/L | 31 | 5.9 | 77 | 400 | 600
Calcium Hardness | mg/L | 67.0122 | 4.0123 | 157.2355 | 375 | 750
Magnesium Hardness | mg/L | 99.3689 | 5.1252 | 148.2371 | 287 | 410
Total Hardness as CaCO3 | mg/L | 166.3811 | 9.1375 | 305.4726 | 662 | 1160
Total Dissolved Solids | mg/L | 470.8102 | 62.077 | 707.9949 | 1050 | 2590
Aluminium as Al | mg/L | 0.008 | 0.004 | 0.008 | 0.3 | 0.5
Arsenic as As | mg/L | <0.006 | <0.006 | <0.006 | 0.01 | 0.05
Chromium as Cr | mg/L | <0.006 | <0.006 | <0.006 | 0.1 | 0.5
Copper as Cu | mg/L | 0.013 | 0.006 | 0.013 | 1 | 2
Iron as Fe | mg/L | 0.01 | 0.02 | 0.011 | 0.2 | 2
Manganese as Mn | mg/L | 0.01 | 0.003 | 0.008 | 0.1 | 1
Lead as Pb | mg/L | <0.010 | <0.010 | <0.010 | 0.02 | 0.05 | 5
Zinc as Zn | mg/L | 0.025 | 0.253 | 0.021 | 5 | 10
Chemistry note: According to these results, all of the parameters tested are within the drinking water limits
Bacteriology: The bacteriology results are reflected on other worksheets in this file.
Signed: ___________________________ | [5 empty] | Date issued: 26 May 2011
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
From: DWAF Domestic use guidelines
Hardness Range | Description of Hardness
0 - 50 | Soft
50 - 100 | Moderately soft
100 - 150 | Slightly hard
150 - 200 | Moderately hard
200 - 300 | Hard
> 300 | Very hard
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za