## Bact1
Test Report
Client: | Kareeberg Municipality |  |  |  | Page 1 of 3
Reference: | 85271
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-06-13
Date sampled: | 2011-06-13
Determinand | Sample number: | SANS 241:2006 specifications | Kareeberg Municipaliteit Carnarvon Hospitaal | Kareeberg Municipaliteit Carnarvon Kliniek | Kareeberg Munisipaliteit Van Wyksvlei Mun Kantoor
| Lab number: |  | U1 | U2 | U3
| Units | value | Value | Value | Value
Heterotrophic plate count | cfu/ml | 100 | 0 | 0 | 2
Total coliforms | cfu/ml | 0 | 0 | 0 | 0
E.coli | cfu/100ml | 0 | 0 | 0 | 0
Bacterial note: All of the parameters tested are within the specifications.
Signed: ___________________________ |  |  |  |  | Date issued: 15 June 2011
H Human
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za

## drink
Test report
Client: | Kareeberg Municipality |  |  |  | Page 2 of 3
Reference: | 85271
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-06-13
Date sampled: | 2011-06-13
Determinand | Sample number: | Carnarvon Hospitaal | Van Wyksvlei Mun. Kantoor | South African National Standard (SANS) 241:2006 for drinking water
| Lab number: | Carnarvon Hospitaal | Van Wyksvlei Mun. Kantoor | Class 1 (Recommended levels) | Class 2 (Maximum allowable for limited time)
| Units | Value | Value | Value | Value
Chemical report
pH |  | 7.87 | 6.36 | 5.5 tot 9.5 | <4 en >10
Electrical conductivity | mS/m | 77.9 | 14.7 | 150 | 370
Calcium as Ca | mg/L | 32 | 0.7 | 150 | 300
Magnesium as Mg | mg/L | 28 | 0.4 | 70 | 100
Sodium as Na | mg/L | 96 | 24 | 200 | 400
Potassium as K | mg/L | 2.18 | 1.53 | 50 | 100
P-Alkalinity | mg/L | 0 | 0
M-Alkalinity | mg/L | 301 | 11.8
Fluoride as F | mg/L | 0.94 | 0.1 | 1 | 1.5
Chloride as Cl | mg/L | 48 | 32 | 200 | 600
Bromide as Br | mg/L | <0.04 | <0.04 | **3 | **6
Nitrate as N | mg/L | 0.87 | <0.05 | 10 | 20
Phosphate as PO4 | mg/L | <0.1 | <0.1 |  | *15.33
Sulphate as SO4 | mg/L | 50 | 5.7 | 400 | 600
Calcium Hardness | mg/L | 80 | 1.75 | 375 | 750
Magnesium Hardness | mg/L | 114.8 | 1.64 | 287 | 410
Total Hardness as CaCO3 | mg/L | 194.8 | 3.39 | 662 | 1160
Total Dissolved Solids | mg/L | 561 | 76.23 | 1050 | 2590
Aluminium as Al | mg/L | 0.006 | 0.004 | 0.3 | 0.5
Arsenic as As | mg/L | <0.006 | <0.006 | 0.01 | 0.05
Chromium as Cr | mg/L | <0.006 | <0.006 | 0.1 | 0.5
Copper as Cu | mg/L | 0.018 | 0.009 | 1 | 2
Iron as Fe | mg/L | 0.015 | 0.03 | 0.2 | 2
Manganese as Mn | mg/L | 0.008 | 0.005 | 0.1 | 1
Lead as Pb | mg/L | <0.010 | <0.010 | 0.02 | 0.05 | 5
Zinc as Zn | mg/L | 0.031 | 0.287 | 5 | 10
Chemistry note: According to these results, all of the parameters tested are within the drinking water limits
Bacteriology: The bacteriology results are reflected on other worksheets in this file.
Signed: ___________________________ |  |  |  |  | Date issued: 5 July 2011
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
From: DWAF Domestic use guidelines
Hardness Range | Description of Hardness
0 - 50 | Soft
50 - 100 | Moderately soft
100 - 150 | Slightly hard
150 - 200 | Moderately hard
200 - 300 | Hard
> 300 | Very hard
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za

## sewage
Test Report
Client: | Kareeberg Municipality |  |  | Page 3 of 3
Reference: | 85271
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-06-13
Date sampled: | 2011-06-13
Determinand | Sample number | Section 39 of the National Water Act of 1998 | Kareeberg Maturation Pond | Kareeberg Anaërobiese Dam
| Lab nr. | General Limit | C1 | C2
| Units | Value | Value | Value
pH |  | 5.5 - 9.5 | 8.74 | 7.81 | 28
Electrical conductivity | mS/m | 70 - 150 mS/m above intake | 138 | 155 | 28
Ammonia (NH3) as N | mg/L | 6 | 21.398 | 74.811 | 65
Chemical Oxygen Demand (COD) | mg/L | 75 | 257 | 368 | 95
Nitrate (NO3)/ Nitrite (NO2) as N | mg/L | 15 | 3.5 | 0.11 | 49
Ortophosphate (PO4) as P | mg/L | 10 | 4.52 | 4.96 | 49
Suspendid Solids(SS) | mg/L | 25 | 108 | 87 | 65
Faecal coliforms | cfu/100ml | 1000 | >2419 | >2419 | 379
E.coli | cfu/100ml |  | 1414 | >2419
Signed: ___________________________ |  |  |  | Date issued: 28 June 2011
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za