## Bact1
Test Report
Client: | Kareeberg Municipality |  |  |  |  | Page 1 of 3
Reference: | 85286
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-07-14
Date sampled: | 2011-07-14
Determinand | Sample number: | SANS 241:2006 specifications | Kareeberg Munisipaliteit Carnarvon Hospitaal | Kareeberg Munisipaliteit Carnarvon Kliniek | Kareeberg Munisipaliteit Van Wyksvlei Mun Kantoor | Kareeberg Munisipaliteit Vosburg Mun Kantoor
| Lab number: |  | K1 | K2 | K3 | K4
| Units | value | Value | Value | Value | Value
Heterotrophic plate count | cfu/ml | 100 | 0 | 0 | 0 | 0
Total coliforms | cfu/ml | 0 | 0 | 0 | 0 | 16
E.coli | cfu/100ml | 0 | 0 | 0 | 0 | 0
Bacterial note: Parameters higher than the specifications, are clearly marked.
Signed: ___________________________ | [5 empty] | Date issued: 16 July 2011
H Human
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za

## drink
Test report
Client: | Kareeberg Municipality |  |  |  |  | Page 2 of 3
Reference: | 85286
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-07-14
Date sampled: | 2011-07-14
Determinand | Sample number: | Carnarvon Hospitaal | Van Wyksvlei Mun Kantoor | Vosburg Mun. Kantoor | South African National Standard (SANS) 241:2006 for drinking water
| Lab number: | Carnarvon Hospitaal | Van Wyksvlei Mun Kantoor | Vosburg Mun. Kantoor | Class 1 (Recommended levels) | Class 2 (Maximum allowable for limited time)
| Units | Value | Value | Value | Value | Value
Chemical report
pH |  | 7.44 | 6.13 | 7.59 | 5.5 tot 9.5 | <4 en >10
Electrical conductivity | mS/m | 82.4 | 20.9 | 108 | 150 | 370
Calcium as Ca | mg/L | 36 | 1.5 | 62.8 | 150 | 300
Magnesium as Mg | mg/L | 32 | 0.84 | 36.6 | 70 | 100
Sodium as Na | mg/L | 101 | 36 | 108 | 200 | 400
Potassium as K | mg/L | 0.97 | 0.75 | 2.25 | 50 | 100
P-Alkalinity | mg/L | 0 | 0 | 0
M-Alkalinity | mg/L | 285 | 19.4 | 315
Fluoride as F | mg/L | 0.09 | 0.2 | 0.83 | 1 | 1.5
Chloride as Cl | mg/L | 58 | 44 | 125 | 200 | 600
Bromide as Br | mg/L | <0.04 | <0.04 | <0.04 | **3 | **6
Nitrate as N | mg/L | 0.7 | 0.09 | 2.1 | 10 | 20
Phosphate as PO4 | mg/L | <0.1 | <0.1 | <1 |  | *15.33
Sulphate as SO4 | mg/L | 56 | 12.1 | 85 | 400 | 600
Calcium Hardness | mg/L | 90 | 4 | 157 | 375 | 750
Magnesium Hardness | mg/L | 131 | 5 | 150 | 287 | 410
Total Hardness as CaCO3 | mg/L | 221 | 8 | 307 | 662 | 1160
Total Dissolved Solids | mg/L | 572 | 115 | 745 | 1050 | 2590
Aluminium as Al | mg/L | 0.007 | <0.004 | 0.01 | 0.3 | 0.5
Arsenic as As | mg/L | <0.006 | <0.006 | <0.006 | 0.01 | 0.05
Chromium as Cr | mg/L | <0.006 | <0.006 | <0.006 | 0.1 | 0.5
Copper as Cu | mg/L | 0.008 | 0.009 | 0.016 | 1 | 2
Iron as Fe | mg/L | 0.01 | 0.019 | 0.014 | 0.2 | 2
Manganese as Mn | mg/L | 0.007 | 0.004 | 0.009 | 0.1 | 1
Lead as Pb | mg/L | <0.010 | <0.010 | 0.011 | 0.02 | 0.05 | 5
Zinc as Zn | mg/L | 0.02 | 0.321 | 0.021 | 5 | 10
Chemistry note: According to these results, all of the parameters tested are within the drinking water limits
Bacteriology: The bacteriology results are reflected on other worksheets in this file.
Signed: ___________________________ | [5 empty] | Date issued: 26 July 2011
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
From: DWAF Domestic use guidelines
Hardness Range | Description of Hardness
0 - 50 | Soft
50 - 100 | Moderately soft
100 - 150 | Slightly hard
150 - 200 | Moderately hard
200 - 300 | Hard
> 300 | Very hard
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za

## sewage
Test Report
Client: | Kareeberg Municipality |  |  | Page 3 of 3
Reference: | 85286
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-07-14
Date sampled: | 2011-07-14
Determinand | Sample number | Section 39 of the National Water Act of 1998 | Kareeberg Anaërobiese Dam | Kareeberg Maturation Pond
| Lab nr. | General Limit | C1 | C2
| Units | Value | Value | Value
pH |  | 5.5 - 9.5 | 7.3 | 8.11
Electrical conductivity | mS/m | 70 - 150 mS/m above intake | 290 | 151
Ammonia (NH3) as N | mg/L | 6 | 185.687 | 39.047
Chemical Oxygen Demand (COD) | mg/L | 75 | 788 | 291
Nitrate (NO3)/ Nitrite (NO2) as N | mg/L | 15 | <0.5 | <0.5
Ortophosphate (PO4) as P | mg/L | 10 | 57.12 | 18.31
Suspendid Solids(SS) | mg/L | 25 | 146 | 84.4
Faecal coliforms | cfu/100ml | 1000 | >2419 | >2419
E.coli | cfu/100ml |  | >2419 | >2419
Signed: ___________________________ |  |  |  | Date issued: 26 July 2011
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za