## Bact1
Test Report
Client: | Kareeberg Municipality |  |  |  |  | Page 1 of 3
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-10-11
Date sampled: | 2011-10-11
Determinand | Sample number: | SANS 241:2006&2011 specifications | Kareeberg Munisipaliteit Carnarvon Hospitaal | Kareeberg Munisipaliteit Carnarvon Kliniek | Kareeberg Munisipaliteit Van Wyksvlei Mun Kantoor | Kareeberg Munisipaliteit Vosburg Mun Kantoor
| Lab number: |  | K1 | K2 | K3 | K4
| Units | value | Value | Value | Value | Value
Heterotrophic plate count | cfu/ml | 1000 | 0 | 0 | 1 | 14
Total coliforms | cfu/ml | 10 | 0 | 0 | 0 | 2
E.coli | cfu/100ml | 0 | 0 | 0 | 0 | 0
Bacterial note: Parameters tested are all within the specifications.
Signed: ___________________________ | [5 empty] | Date issued: 17 October 2011
H Human
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za

## drink
Test report
Client: | Kareeberg Municipality |  |  |  |  | Page 2 of 3
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-10-11
Date sampled: | 2011-10-11
Determinand | Sample number: | Carnarvon Hospital | Van Wyksvlei Mun Kantoor | Vosburg Mun. Kantoor | South African National Standard (SANS) 241:2006&2011 for drinking water
| Lab number: | 517 | 518 | 519 | Class 1 (Recommended levels) | Class 2 (Maximum allowable for limited time)
| Units | Value | Value | Value | Value | Value
Chemical report
pH |  | 7.85 | 6.7 | 7.67 | 5.5 tot 9.7
Electrical conductivity | mS/m | 112 | 22.4 | 121 | 170
Calcium as Ca | mg/L | 43.083 | 1.8691 | 87.2324 | 150 | 300
Magnesium as Mg | mg/L | 38.7971 | 1.0538 | 46.8762 | 70 | 100
Sodium as Na | mg/L | 118.6109 | 42.1512 | 107.3938 | 200
Potassium as K | mg/L | 0.75597 | 0.32692 | 2.3551 | 50 | 100
P-Alkalinity | mg/L | 0 | 0 | 0
M-Alkalinity | mg/L | 346 | 19.6 | 341
Fluoride as F | mg/L | 0.7254 | 0.2484 | <0.1 | 1.5
Chloride as Cl | mg/L | 96.8816 | 51.5885 | 139.4497 | 200 | 600
Bromide as Br | mg/L | <0.4 | 0.1486 | -0.4 | **3 | **6
Nitrate as N | mg/L | 0.9795 | <0.05 | 3.3195 | 11
Phosphate as PO4 | mg/L | -1 | -0.1 | -1 |  | *15.33
Sulphate as SO4 | mg/L | 87.0513 | 11.8464 | 91.8705 | 500
Calcium Hardness | mg/L | 107.7076 | 4.6728 | 218.081 | 375 | 750
Magnesium Hardness | mg/L | 159.0681 | 4.3205 | 192.1926 | 287 | 410
Total Hardness as CaCO3 | mg/L | 266.7757 | 8.9934 | 410.2736 | 662 | 1160
Total Dissolved Solids | mg/L | 734.4127 | 128.4687 | 828.9434 | 1200
Aluminium as Al | mg/L | 0.007 | <0.004 | 0.008 | 0.3
Arsenic as As | mg/L | <0.006 | <0.006 | <0.006 | 0.01
Chromium as Cr | mg/L | <0.006 | <0.006 | <0.006 | 0.05
Copper as Cu | mg/L | 0.045 | 0.009 | 0.022 | 2
Iron as Fe | mg/L | 0.01 | 0.02 | 0.011 | 2
Manganese as Mn | mg/L | 0.014 | 0.004 | 0.019 | 0.5
Lead as Pb | mg/L | <0.010 | <0.010 | <0.010 | 0.01 |  | 5
Zinc as Zn | mg/L | 0.028 | 0.354 | 0.018 | 5
Chemistry note: According to these results, all of the parameters tested are within the drinking water limits.
Bacteriology: The bacteriology results are reflected on other worksheets in this file.
Signed: ___________________________ | [5 empty] | Date issued: 28 October 2011
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
From: DWAF Domestic use guidelines
Hardness Range | Description of Hardness
0 - 50 | Soft
50 - 100 | Moderately soft
100 - 150 | Slightly hard
150 - 200 | Moderately hard
200 - 300 | Hard
> 300 | Very hard
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za

## sewage
Test Report
Client: | Kareeberg Municipality |  |  | page 3 of 3
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-10-11
Date sampled: | 2011-10-11
Determinand | Sample number | Section 39 of the National Water Act of 1998 | Carnarvon Anaerobiese damme | Carnarvon Maturation Pond
| Lab nr. | General Limit | 520 | 521
| Units | Value | Value | Value
pH |  | 5.5 - 9.5 | 7.32 | 8.04
Electrical conductivity | mS/m | 70 - 150 mS/m above intake | 172 | 163
Ammonia (NH3) as N | mg/L | 6 | 28.774 | 26.338
Chemical Oxygen Demand (COD) | mg/L | 75 | 363 | 387
Nitrate (NO3)/ Nitrite (NO2) as N | mg/L | 15 | <0.5 | <0.5
Ortophosphate (PO4) | mg/L | 30.66 | 7.4 | 16.44
Suspendid Solids(SS) | mg/L | 25 | 185 | 187
Faecal coliforms | cfu/100ml | 1000 | >2419 | >2419
E.coli | cfu/100ml |  | >2419 | 2419
Signed: ___________________________ |  |  |  | Date issued: 17 October 2011
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za