## Bact1
Test Report
Client: | Kareeberg Municipality |  |  |  |  | Page 1 of 3
Reference:
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-08-16
Date sampled: | 2011-08-16
Determinand | Sample number: | SANS 241:2006&2011 specifications | Kareeberg Munisipaliteit Carnarvon Hospitaal | Kareeberg Munisipaliteit Carnarvon Kliniek | Kareeberg Munisipaliteit Van Wyksvlei Mun Kantoor | Kareeberg Munisipaliteit Vosburg Mun Kantoor
| Lab number: |  | K1 | K2 | K3 | K4
| Units | value | Value | Value | Value | Value
Heterotrophic plate count | cfu/ml | 1000 | 0 | 0 | >2500 | 13
Total coliforms | cfu/ml | 10 | 0 | 0 | 0 | 4
E.coli | cfu/100ml | 0 | 0 | 0 | 0 | 0
Bacterial note: Parameters higher than the specifications, are clearly marked.
Signed: ___________________________ | [5 empty] | Date issued: 18 August 2011
H Human
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za

## drink
Test report
Client: | Kareeberg Municipality |  |  |  | Page 2 of 3
Reference:
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-08-16
Date sampled: | 2011-08-16
Determinand | Sample number: | Carnarvon Hospitaal | Vosburg Mun. Kantoor | South African National Standard (SANS) 241:2006 for drinking water
| Lab number: | Carnarvon Hospitaal | Vosburg Mun. Kantoor | Class 1 (Recommended levels) | Class 2 (Maximum allowable for limited time)
| Units | Value | Value | Value | Value
Chemical report
pH |  | 7.77 | 7.62 | 5.5 tot 9.5 | <4 en >10
Electrical conductivity | mS/m | 89.6 | 109 | 150 | 370
Calcium as Ca | mg/L | 39 | 64 | 150 | 300
Magnesium as Mg | mg/L | 33 | 38 | 70 | 100
Sodium as Na | mg/L | 106 | 110 | 200 | 400
Potassium as K | mg/L | 1.27 | 2.51 | 50 | 100
P-Alkalinity | mg/L | 0 | 0
M-Alkalinity | mg/L | 311 | 321
Fluoride as F | mg/L | 0.9 | 0.32 | 1 | 1.5
Chloride as Cl | mg/L | 68 | 110 | 200 | 600
Bromide as Br | mg/L | <0.04 | <0.04 | **3 | **6
Nitrate as N | mg/L | 0.76 | 2.01 | 10 | 20
Phosphate as PO4 | mg/L | <0.1 | <1 |  | *15.33
Sulphate as SO4 | mg/L | 65 | 79 | 400 | 600
Calcium Hardness | mg/L | 97.5 | 160 | 375 | 750
Magnesium Hardness | mg/L | 135.3 | 155.8 | 287 | 410
Total Hardness as CaCO3 | mg/L | 232.8 | 315.8 | 662 | 1160
Total Dissolved Solids | mg/L | 627.5342 | 733.7275 | 1050 | 2590
Aluminium as Al | mg/L | 0.007 | 0.005 | 0.3 | 0.5
Arsenic as As | mg/L | <0.006 | <0.006 | 0.01 | 0.05
Chromium as Cr | mg/L | <0.006 | <0.006 | 0.1 | 0.5
Copper as Cu | mg/L | 0.011 | 0.012 | 1 | 2
Iron as Fe | mg/L | 0.013 | 0.014 | 0.2 | 2
Manganese as Mn | mg/L | 0.005 | 0.005 | 0.1 | 1
Lead as Pb | mg/L | <0.010 | <0.010 | 0.02 | 0.05 | 5
Zinc as Zn | mg/L | 0.015 | 0.012 | 5 | 10
Chemistry note: According to these results, all of the parameters tested are within the drinking water limits
Bacteriology: The bacteriology results are reflected on other worksheets in this file.
Signed: ___________________________ |  |  |  |  | Date issued: 31 August 2011
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
From: DWAF Domestic use guidelines
Hardness Range | Description of Hardness
0 - 50 | Soft
50 - 100 | Moderately soft
100 - 150 | Slightly hard
150 - 200 | Moderately hard
200 - 300 | Hard
> 300 | Very hard
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za

## sewage
Test Report
Client: | Kareeberg Municipality
Reference: |  |  |  | page 3 of 3
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2011-08-16
Date sampled: | 2011-08-16
Determinand | Sample number | Section 39 of the National Water Act of 1998 | Kareeberg Maturation Pond | Kareeberg Anaerobiese Damme
| Lab nr. | General Limit | K3 | K4
| Units | Value | Value | Value
pH |  | 5.5 - 9.5 | 8.47 | 7.55
Electrical conductivity | mS/m | 70 - 150 mS/m above intake | 145 | 165
Ammonia (NH3) as N | mg/L | 6 | 25.184 | 58.289
Chemical Oxygen Demand (COD) | mg/L | 75 | 308 | 331
Nitrate (NO3)/ Nitrite (NO2) as N | mg/L | 15 | <0.5 | <0.5
Ortophosphate (PO4) as P | mg/L | 10 | 5.92 | 7.14
Suspendid Solids(SS) | mg/L | 25 | 127 | 72.2
Faecal coliforms | cfu/100ml | 1000 | >2419 | >2419
E.coli | cfu/100ml |  | >2419 | >2419
Signed: ___________________________ |  |  |  | Date issued: 5 September 2011
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za