## Bact1
Test Report
Client: | Kareeberg Municipality |  |  |  |  | Page 1 of 2
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2012-01-16
Date sampled: | 2012-01-16
Determinand | Sample number: | SANS 241:2006&2011 specifications | Carnavarvon Kliniek | Carnarvon Munisipaliteit | Van Wyksvlei Mun Kantoor | Vosburg Mun Kantoor
| Lab number: |  | 145 | 146 | 147 | 148
| Units | value | Value | Value | Value | Value
Heterotrophic plate count | cfu/ml | 1000 | 28 | 23 | 2 | >2500
Total coliforms | cfu/ml | 10 | 1 | 4 | 4 | 0
E.coli | cfu/100ml | 0 | 0 | 0 | 0 | 0
Bacterial note: Parameters tested are all within the specifications.
Signed: ___________________________ | [5 empty] | Date issued: 18 January 2012
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za

## drink
Test report
Client: | Kareeberg Municipality |  |  |  |  | Page 2 of 2
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2012-01-16
Date sampled: | 2012-01-16
Determinand | Sample number: | Carnarvon Hospital | Van Wyksvlei Mun Kantoor | Vosburg Mun. Kantoor | South African National Standard (SANS) 241:2006&2011 for drinking water
| Lab number: | 146 | 147 | 148 | Class 1 (Recommended levels) | Class 2 (Maximum allowable for limited time)
| Units | Value | Value | Value | Value | Value
Chemical report
pH |  | 7.94 | 6.75 | 7.63 | 5.5 tot 9.7
Electrical conductivity | mS/m | 112 | 3.93 | 134 | 170
Calcium as Ca | mg/L | 53.9472 | 0.50978 | 96.5893 | 150 | 300
Magnesium as Mg | mg/L | 50.565 | 0.11593 | 53.6442 | 70 | 100
Sodium as Na | mg/L | 149.4434 | 7.7706 | 131.2703 | 200
Potassium as K | mg/L | 1.3068 | 0.82832 | 3.1265 | 50 | 100
P-Alkalinity | mg/L | 0 | 0 | 0
M-Alkalinity | mg/L | 364 | 8.5 | 361
Fluoride as F | mg/L | 0.99 | 0.02 | 0.15 | 1.5
Chloride as Cl | mg/L | 98 | 7.7 | 157 | 200 | 600
Bromide as Br | mg/L | <0.4 | <0.04 | <0.04 | **3 | **6
Nitrate as N | mg/L | 0.66 | 0.12 | 4.01 | 11
Phosphate as PO4 | mg/L | <1 | <0.1 | 1.15 |  | *15.33
Sulphate as SO4 | mg/L | 105 | 0.54 | 107 | 500
Calcium Hardness | mg/L | 134.8681 | 1.2744 | 241.4733 | 375 | 750
Magnesium Hardness | mg/L | 207.3164 | 0.4753 | 219.9411 | 287 | 410
Total Hardness as CaCO3 | mg/L | 342.1845 | 1.7498 | 461.4144 | 662 | 1160
Total Dissolved Solids | mg/L | 826.174 | 26.5159 | 927.531 | 1200
Aluminium as Al | mg/L | 0.016024 | 0.025273 | 0.011397 | 0.3
Arsenic as As | mg/L | <0.006 | <0.006 | <0.006 | 0.01
Chromium as Cr | mg/L | <0.006 | <0.006 | <0.006 | 0.05
Copper as Cu | mg/L | 0.010647 | 0.0031927 | 0.0096329 | 2
Iron as Fe | mg/L | <0.004 | 0.038954 | <0.004 | 2
Manganese as Mn | mg/L | 0.021992 | 0.0016292 | 0.019996 | 0.5
Lead as Pb | mg/L | <0.010 | <0.010 | <0.010 | 0.01 |  | 5
Zinc as Zn | mg/L | 0.021307 | 0.018486 | 0.016118 | 5
Chemistry note: According to these results, all of the parameters tested are within the drinking water limits.
Bacteriology: The bacteriology results are reflected on other worksheets in this file.
Signed: ___________________________ | [5 empty] | Date issued: 2 February 2012
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
From: DWAF Domestic use guidelines
Hardness Range | Description of Hardness
0 - 50 | Soft
50 - 100 | Moderately soft
100 - 150 | Slightly hard
150 - 200 | Moderately hard
200 - 300 | Hard
> 300 | Very hard
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za