## Bact1
Test Report
Client: | Kareeberg Municipality |  |  |  |  | Page 1 of 3
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2012-02-21
Date sampled: | 2012-02-20
Determinand | Sample number: | SANS 241:2006&2011 specifications | Carnavarvon Hospitaal | Carnarvon Kliniek | Van Wyksvlei Mun Kantoor | Vosburg Mun Kantoor
| Lab number: |  | K1 | K2 | K3 | K4
| Units | value | Value | Value | Value | Value
Heterotrophic plate count | cfu/ml | 1000 | 13 | 15 | 433 | 3
Total coliforms | cfu/ml | 10 | 4 | 2 | >201 | 18
E.coli | cfu/100ml | 0 | 0 | 0 | 18 | 0
Bacterial note: Parameters tested are all within the specifications.
Signed: ___________________________ | [5 empty] | Date issued: 24 February 2012
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za

## drink
Test report
Client: | Kareeberg Municipality |  |  |  |  | Page 2 of 3
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2012-02-21
Date sampled: | 2012-02-20
Determinand | Sample number: | Carnarvon Hospital | Van Wyksvlei Mun Kantoor | Vosburg Mun. Kantoor | South African National Standard (SANS) 241:2006&2011 for drinking water
| Lab number: | Ka1 | Ka2 | Ka3 | Class 1 (Recommended levels) | Class 2 (Maximum allowable for limited time)
| Units | Value | Value | Value | Value | Value
Chemical report
pH |  | 8.08 | 8.04 | 7.79 | 5.5 tot 9.7
Electrical conductivity | mS/m | 91.5 | 59.8 | 135 | 170
Calcium as Ca | mg/L | 47.0737 | 38.6707 | 99.0355 | 150 | 300
Magnesium as Mg | mg/L | 38.2218 | 9.4696 | 53.9769 | 70 | 100
Sodium as Na | mg/L | 122.1925 | 71.8824 | 110.347 | 200
Potassium as K | mg/L | 0.7279 | 1.1304 | 2.6586 | 50 | 100
P-Alkalinity | mg/L | 0 | 0 | 0
M-Alkalinity | mg/L | 331 | 97 | 357
Fluoride as F | mg/L | 0.84 | 0.04 | 0.05 | 1.5
Chloride as Cl | mg/L | 96 | 75 | 179 | 200 | 600
Bromide as Br | mg/L | <0.4 | <0.04 | <0.04 | **3 | **6
Nitrate as N | mg/L | 4.67 | 0.15 | 4.74 | 11
Phosphate as PO4 | mg/L | <1 | <0.1 | 1.15 |  | *15.33
Sulphate as SO4 | mg/L | 76 | 106 | 104 | 500
Calcium Hardness | mg/L | 117.6842 | 96.6767 | 247.5887 | 375 | 750
Magnesium Hardness | mg/L | 156.7092 | 38.8255 | 221.3053 | 287 | 410
Total Hardness as CaCO3 | mg/L | 274.3935 | 135.5021 | 468.894 | 662 | 1160
Total Dissolved Solids | mg/L | 732.7281 | 399.8571 | 927.0501 | 1200
Aluminium as Al | mg/L | 0.0032958 | 0.0082701 | 0.0032113 | 0.3
Arsenic as As | mg/L | <0.006 | <0.006 | <0.006 | 0.01
Chromium as Cr | mg/L | <0.006 | <0.006 | <0.006 | 0.05
Copper as Cu | mg/L | 0.0021102 | 0.0055153 | 0.0025544 | 2
Iron as Fe | mg/L | 0.004597 | 0.01165 | 0.0044282 | 2
Manganese as Mn | mg/L | 0.002 | 0.012 | 0.002 | 0.5
Lead as Pb | mg/L | <0.010 | <0.010 | <0.010 | 0.01 |  | 5
Zinc as Zn | mg/L | 0.018 | 0.2 | 0.012 | 5
Chemistry note: According to these results, all of the parameters tested are within the drinking water limits.
Bacteriology: The bacteriology results are reflected on other worksheets in this file.
Signed: ___________________________ | [5 empty] | Date issued: 24 February 2012
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
From: DWAF Domestic use guidelines
Hardness Range | Description of Hardness
0 - 50 | Soft
50 - 100 | Moderately soft
100 - 150 | Slightly hard
150 - 200 | Moderately hard
200 - 300 | Hard
> 300 | Very hard
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za

## Sewage
Test Report
Client: | Kareeberg Municipality |  |  | page 3 of 3
Contact: | Frans Groenewald
Delivered by: | Frans Groenewald
Date delivered | 2012-02-21
Date sampled: | 2012-02-20
Determinand | Sample number | Section 39 of the National Water Act of 1998 | Anaerobiese damme | Maturation Pond
| Lab nr. | General Limit | K5 | K6
| Units | Value | Value | Value
pH |  | 5.5 - 9.5 | 8.13 | 8.98
Electrical conductivity | mS/m | 70 - 150 mS/m above intake | 147 | 175
Ammonia (NH3) as N | mg/L | 6
Chemical Oxygen Demand (COD) | mg/L | 75 | 319 | 202
Nitrate (NO3)/ Nitrite (NO2) as N | mg/L | 15 | <0.5 | <0.5
Ortophosphate (PO4) | mg/L | 30.66 | <1 | <1
Ortophosphate (PO4) as P | mg/L | 10 | <0.33 | <0.33
Suspendid Solids(SS) | mg/L | 25
Faecal coliforms | cfu/100ml | 1000 | >2419 | >2419
E.coli | cfu/100ml |  | >2419 | >2419
Signed: ___________________________ |  |  |  | Date issued: 24 February 2012
L Cruywagen
This report relates only to the samples supplied to the Laboratory at the Insitute for Groundwater Studies
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za
Institute for Groundwater Studies
IGS Laboratory Services
University of the Free State
* 339, BLOEMFONTEIN, 9300
( +27-(0)51 - 401 2317
7: +27-(0)51 - 444 6538 e-mail: igslab@ufs.ac.za